## List of Voltages
Bus | 1 | Voltage: | 1.05 | Angle: | 0
Bus | 2 | Voltage: | 1.045 | Angle: | -3.289
Bus | 3 | Voltage: | 1.01 | Angle: | -9.4065
Bus | 4 | Voltage: | 1.0267 | Angle: | -6.4469
Bus | 5 | Voltage: | 1.0304 | Angle: | -5.4432
Bus | 6 | Voltage: | 1.0231 | Angle: | -7.9323
Bus | 7 | Voltage: | 0.9899 | Angle: | -10.6247
Bus | 8 | Voltage: | 0.98714 | Angle: | -10.4719
Bus | 9 | Voltage: | 0.99998 | Angle: | -9.3793
Bus | 10 | Voltage: | 1.06 | Angle: | -6.8135
Bus | 11 | Voltage: | 1.0245 | Angle: | -8.137
Bus | 12 | Voltage: | 1.04 | Angle: | -9.2402

## Power Produce at Gen.
Bus | 1 | P MW: | 145.6856 | Q MVAr: | -26.0757
Bus | 2 | P MW: | 18.3094 | Q MVAr: | 26.9157
Bus | 3 | P MW: | -61.1975 | Q MVAr: | 2.7978
Bus | 4 | P MW: | 27.8033 | Q MVAr: | 11.5381
Bus | 5 | P MW: | 12.1012 | Q MVAr: | 18.4362
Bus | 6 | P MW: | -57.8108 | Q MVAr: | 3.9146
Bus | 7 | P MW: | -7.5844 | Q MVAr: | -1.584
Bus | 8 | P MW: | -13.5006 | Q MVAr: | -8.4969
Bus | 9 | P MW: | -29.4998 | Q MVAr: | -13.5982
Bus | 10 | P MW: | -8.9995 | Q MVAr: | -5.7996
Bus | 11 | P MW: | -4.3015 | Q MVAr: | -2.0984
Bus | 12 | P MW: | -13.4983 | Q MVAr: | -5.799

## Power Flow at Line
Line: | 1 | to | 2 | P MW: | 29.1373 | Q MVAr: | 263.6412 | S MVA: | 265.2465
Line: | 1 | to | 5 | P MW: | 3.9289 | Q MVAr: | -92.8822 | S MVA: | 92.9653
Line: | 2 | to | 3 | P MW: | -2.2384 | Q MVAr: | -119.0306 | S MVA: | 119.0516
Line: | 2 | to | 4 | P MW: | -4.4112 | Q MVAr: | -169.7703 | S MVA: | 169.8276
Line: | 2 | to | 5 | P MW: | -3.416 | Q MVAr: | -165.3032 | S MVA: | 165.3385
Line: | 3 | to | 4 | P MW: | 7.1529 | Q MVAr: | 57.733 | S MVA: | 58.1744
Line: | 4 | to | 5 | P MW: | -11.5234 | Q MVAr: | 278.4999 | S MVA: | 278.7382
Line: | 4 | to | 7 | P MW: | 0 | Q MVAr: | 0 | S MVA: | 0
Line: | 5 | to | 6 | P MW: | 0 | Q MVAr: | 0 | S MVA: | 0
Line: | 6 | to | 9 | P MW: | 2.823 | Q MVAr: | -159.9574 | S MVA: | 159.9823
Line: | 6 | to | 10 | P MW: | -3.2311 | Q MVAr: | -8.9139 | S MVA: | 9.4814
Line: | 6 | to | 11 | P MW: | -1.1428 | Q MVAr: | -59.4336 | S MVA: | 59.4446
Line: | 7 | to | 8 | P MW: | -0.60134 | Q MVAr: | -308.6546 | S MVA: | 308.6552
Line: | 7 | to | 12 | P MW: | -3.5092 | Q MVAr: | 12.9356 | S MVA: | 13.4031
Line: | 8 | to | 9 | P MW: | -1.1423 | Q MVAr: | -177.8614 | S MVA: | 177.865
Line: | 10 | to | 11 | P MW: | 4.0428 | Q MVAr: | 213.8009 | S MVA: | 213.8391
Line: | 11 | to | 12 | P MW: | 1.6126 | Q MVAr: | 90.6685 | S MVA: | 90.6828

## Line Check
Line | 1 | to Line | 2 | has exceeded normal operation limit
Line | 1 | to Line | 5 | has not exceeded normal operation limit
Line | 2 | to Line | 3 | has not exceeded normal operation limit
Line | 2 | to Line | 4 | has not exceeded normal operation limit
Line | 2 | to Line | 5 | has not exceeded normal operation limit
Line | 3 | to Line | 4 | has not exceeded normal operation limit
Line | 4 | to Line | 5 | has not exceeded normal operation limit
Line | 4 | to Line | 7 | has not exceeded normal operation limit
Line | 5 | to Line | 6 | has not exceeded normal operation limit
Line | 6 | to Line | 9 | has not exceeded normal operation limit
Line | 6 | to Line | 10 | has not exceeded normal operation limit
Line | 6 | to Line | 11 | has not exceeded normal operation limit
Line | 7 | to Line | 8 | has not exceeded normal operation limit
Line | 7 | to Line | 12 | has not exceeded normal operation limit
Line | 8 | to Line | 9 | has not exceeded normal operation limit
Line | 10 | to Line | 11 | has not exceeded normal operation limit
Line | 11 | to Line | 12 | has not exceeded normal operation limit

## Voltage Check
Bus | 1 | has not exceeded normal operating limits
Bus | 2 | has not exceeded normal operating limits
Bus | 3 | has not exceeded normal operating limits
Bus | 4 | has not exceeded normal operating limits
Bus | 5 | has not exceeded normal operating limits
Bus | 6 | has not exceeded normal operating limits
Bus | 7 | has not exceeded normal operating limits
Bus | 8 | has not exceeded normal operating limits
Bus | 9 | has not exceeded normal operating limits
Bus | 10 | has exceeded normal operating limits
Bus | 11 | has not exceeded normal operating limits
Bus | 12 | has not exceeded normal operating limits