## List of Voltages
Bus | 1 | Voltage: | 1.05 | Angle: | 0
Bus | 2 | Voltage: | 1.045 | Angle: | -5.7759
Bus | 3 | Voltage: | 1.01 | Angle: | -11.8486
Bus | 4 | Voltage: | 1.0274 | Angle: | -8.3471
Bus | 5 | Voltage: | 1.0308 | Angle: | -7.1878
Bus | 6 | Voltage: | 1.0233 | Angle: | -9.7092
Bus | 7 | Voltage: | 0.99 | Angle: | -12.4463
Bus | 8 | Voltage: | 0.98725 | Angle: | -12.2855
Bus | 9 | Voltage: | 1.0001 | Angle: | -11.1745
Bus | 10 | Voltage: | 1.06 | Angle: | -8.5874
Bus | 11 | Voltage: | 1.0246 | Angle: | -9.9187
Bus | 12 | Voltage: | 1.04 | Angle: | -11.0418

## Power Produce at Gen.
Bus | 1 | P MW: | 147.2691 | Q MVAr: | -26.7129
Bus | 2 | P MW: | 18.3151 | Q MVAr: | 31.68
Bus | 3 | P MW: | -61.1967 | Q MVAr: | 4.0337
Bus | 4 | P MW: | 27.8038 | Q MVAr: | 11.411
Bus | 5 | P MW: | 12.1014 | Q MVAr: | 18.3785
Bus | 6 | P MW: | -57.8127 | Q MVAr: | 3.9168
Bus | 7 | P MW: | -7.5789 | Q MVAr: | -1.5738
Bus | 8 | P MW: | -13.5007 | Q MVAr: | -8.4965
Bus | 9 | P MW: | -29.4997 | Q MVAr: | -13.5981
Bus | 10 | P MW: | -8.9995 | Q MVAr: | -5.7995
Bus | 11 | P MW: | -4.3017 | Q MVAr: | -2.0983
Bus | 12 | P MW: | -13.498 | Q MVAr: | -5.7989

## Power Flow at Line
Line: | 1 | to | 2 | P MW: | -188.6013 | Q MVAr: | -860.7213 | S MVA: | 881.1422
Line: | 1 | to | 5 | P MW: | -52.8119 | Q MVAr: | -468.6535 | S MVA: | 471.6197
Line: | 2 | to | 3 | P MW: | -65.7304 | Q MVAr: | -514.5429 | S MVA: | 518.7242
Line: | 2 | to | 4 | P MW: | -156.2033 | Q MVAr: | -556.8461 | S MVA: | 578.3399
Line: | 2 | to | 5 | P MW: | -169.4012 | Q MVAr: | -563.8196 | S MVA: | 588.7184
Line: | 3 | to | 4 | P MW: | -147.3845 | Q MVAr: | -28.1588 | S MVA: | 150.0504
Line: | 4 | to | 5 | P MW: | -770.6018 | Q MVAr: | -2270.2081 | S MVA: | 2397.4303
Line: | 4 | to | 7 | P MW: | 13.0735 | Q MVAr: | -182.4181 | S MVA: | 182.886
Line: | 5 | to | 6 | P MW: | 18.413 | Q MVAr: | -418.1393 | S MVA: | 418.5445
Line: | 6 | to | 9 | P MW: | -189.3029 | Q MVAr: | -423.979 | S MVA: | 464.3208
Line: | 6 | to | 10 | P MW: | -172.236 | Q MVAr: | -341.1941 | S MVA: | 382.2024
Line: | 6 | to | 11 | P MW: | -322.5783 | Q MVAr: | -641.0528 | S MVA: | 717.6388
Line: | 7 | to | 8 | P MW: | -384.2198 | Q MVAr: | -1012.0144 | S MVA: | 1082.4962
Line: | 7 | to | 12 | P MW: | -154.2165 | Q MVAr: | -308.1846 | S MVA: | 344.6164
Line: | 8 | to | 9 | P MW: | -194.1041 | Q MVAr: | -431.0457 | S MVA: | 472.7333
Line: | 10 | to | 11 | P MW: | -264.5732 | Q MVAr: | -250.7972 | S MVA: | 364.5521
Line: | 11 | to | 12 | P MW: | -116.2986 | Q MVAr: | -249.0074 | S MVA: | 274.8273

## Line Check
Line | 1 | to Line | 2 | has exceeded normal operation limit
Line | 1 | to Line | 5 | has exceeded normal operation limit
Line | 2 | to Line | 3 | has not exceeded normal operation limit
Line | 2 | to Line | 4 | has not exceeded normal operation limit
Line | 2 | to Line | 5 | has not exceeded normal operation limit
Line | 3 | to Line | 4 | has not exceeded normal operation limit
Line | 4 | to Line | 5 | has not exceeded normal operation limit
Line | 4 | to Line | 7 | has not exceeded normal operation limit
Line | 5 | to Line | 6 | has not exceeded normal operation limit
Line | 6 | to Line | 9 | has not exceeded normal operation limit
Line | 6 | to Line | 10 | has not exceeded normal operation limit
Line | 6 | to Line | 11 | has not exceeded normal operation limit
Line | 7 | to Line | 8 | has not exceeded normal operation limit
Line | 7 | to Line | 12 | has not exceeded normal operation limit
Line | 8 | to Line | 9 | has not exceeded normal operation limit
Line | 10 | to Line | 11 | has not exceeded normal operation limit
Line | 11 | to Line | 12 | has not exceeded normal operation limit

## Voltage Check
Bus | 1 | has not exceeded normal operating limits
Bus | 2 | has not exceeded normal operating limits
Bus | 3 | has not exceeded normal operating limits
Bus | 4 | has not exceeded normal operating limits
Bus | 5 | has not exceeded normal operating limits
Bus | 6 | has not exceeded normal operating limits
Bus | 7 | has not exceeded normal operating limits
Bus | 8 | has not exceeded normal operating limits
Bus | 9 | has not exceeded normal operating limits
Bus | 10 | has exceeded normal operating limits
Bus | 11 | has not exceeded normal operating limits
Bus | 12 | has not exceeded normal operating limits

## Convergence Record
Iteration | Maximum P Mismatch | Location of P Mismatch | Maximum Q Mismatch | Location of Q Mismatch
1 | 0.03508 | 1 | 0.058125 | 6
2 | 0.0002111 | 6 | 0.0002623 | 6