## List of Voltages
Bus | 1 | Voltage: | 1.05 | Angle: | 0
Bus | 2 | Voltage: | 1.045 | Angle: | -3.2677
Bus | 3 | Voltage: | 1.01 | Angle: | -9.28
Bus | 4 | Voltage: | 1.0339 | Angle: | -6.5657
Bus | 5 | Voltage: | 1.039 | Angle: | -5.5592
Bus | 6 | Voltage: | 1.0536 | Angle: | -7.7724
Bus | 7 | Voltage: | 1.0508 | Angle: | -10.8212
Bus | 8 | Voltage: | 1.0522 | Angle: | -10.7909
Bus | 9 | Voltage: | 1.0521 | Angle: | -9.5863
Bus | 10 | Voltage: | 1.06 | Angle: | -5.6062
Bus | 11 | Voltage: | 1.0475 | Angle: | -7.8424
Bus | 12 | Voltage: | 1.04 | Angle: | -8.1152

## Power Produce at Gen.
Bus | 1 | P MW: | 145.4457 | Q MVAr: | -29.9439
Bus | 2 | P MW: | 18.3106 | Q MVAr: | 17.4126
Bus | 3 | P MW: | -61.1973 | Q MVAr: | 1.6414
Bus | 4 | P MW: | 27.816 | Q MVAr: | -11.6607
Bus | 5 | P MW: | 12.1119 | Q MVAr: | -11.6013
Bus | 6 | P MW: | -57.815 | Q MVAr: | -3.8795
Bus | 7 | P MW: | -7.5772 | Q MVAr: | 1.6235
Bus | 8 | P MW: | -13.4867 | Q MVAr: | 8.5154
Bus | 9 | P MW: | -29.5042 | Q MVAr: | 13.6169
Bus | 10 | P MW: | -9.0089 | Q MVAr: | 5.806
Bus | 11 | P MW: | -4.301 | Q MVAr: | 2.1067
Bus | 12 | P MW: | -13.4919 | Q MVAr: | 5.8062

## Power Flow at Line
Line: | 1 | to | 2 | P MW: | 28.9446 | Q MVAr: | 263.4685 | S MVA: | 265.0537
Line: | 1 | to | 5 | P MW: | 4.0255 | Q MVAr: | -93.5178 | S MVA: | 93.6044
Line: | 2 | to | 3 | P MW: | -2.1774 | Q MVAr: | -119.0618 | S MVA: | 119.0817
Line: | 2 | to | 4 | P MW: | -4.6617 | Q MVAr: | -171.0839 | S MVA: | 171.1474
Line: | 2 | to | 5 | P MW: | -3.6794 | Q MVAr: | -166.8588 | S MVA: | 166.8993
Line: | 3 | to | 4 | P MW: | 6.5974 | Q MVAr: | 57.5742 | S MVA: | 57.951
Line: | 4 | to | 5 | P MW: | -11.7326 | Q MVAr: | 282.7567 | S MVA: | 283
Line: | 4 | to | 7 | P MW: | 0 | Q MVAr: | 0 | S MVA: | 0
Line: | 5 | to | 6 | P MW: | 0 | Q MVAr: | 0 | S MVA: | 0
Line: | 6 | to | 9 | P MW: | 3.7973 | Q MVAr: | -172.4391 | S MVA: | 172.4809
Line: | 6 | to | 10 | P MW: | -6.4419 | Q MVAr: | -12.2818 | S MVA: | 13.8687
Line: | 6 | to | 11 | P MW: | -0.41086 | Q MVAr: | -61.7892 | S MVA: | 61.7905
Line: | 7 | to | 8 | P MW: | -0.13447 | Q MVAr: | -348.6865 | S MVA: | 348.6865
Line: | 7 | to | 12 | P MW: | -7.2534 | Q MVAr: | 10.1455 | S MVA: | 12.4717
Line: | 8 | to | 9 | P MW: | -1.4203 | Q MVAr: | -199.5637 | S MVA: | 199.5687
Line: | 10 | to | 11 | P MW: | 7.1125 | Q MVAr: | 221.1589 | S MVA: | 221.2732
Line: | 11 | to | 12 | P MW: | 0.40151 | Q MVAr: | 91.5218 | S MVA: | 91.5227

## Line Check
Line | 1 | to Line | 2 | has exceeded normal operation limit
Line | 1 | to Line | 5 | has not exceeded normal operation limit
Line | 2 | to Line | 3 | has not exceeded normal operation limit
Line | 2 | to Line | 4 | has not exceeded normal operation limit
Line | 2 | to Line | 5 | has not exceeded normal operation limit
Line | 3 | to Line | 4 | has not exceeded normal operation limit
Line | 4 | to Line | 5 | has not exceeded normal operation limit
Line | 4 | to Line | 7 | has not exceeded normal operation limit
Line | 5 | to Line | 6 | has not exceeded normal operation limit
Line | 6 | to Line | 9 | has not exceeded normal operation limit
Line | 6 | to Line | 10 | has not exceeded normal operation limit
Line | 6 | to Line | 11 | has not exceeded normal operation limit
Line | 7 | to Line | 8 | has not exceeded normal operation limit
Line | 7 | to Line | 12 | has not exceeded normal operation limit
Line | 8 | to Line | 9 | has not exceeded normal operation limit
Line | 10 | to Line | 11 | has not exceeded normal operation limit
Line | 11 | to Line | 12 | has not exceeded normal operation limit

## Voltage Check
Bus | 1 | has not exceeded normal operating limits
Bus | 2 | has not exceeded normal operating limits
Bus | 3 | has not exceeded normal operating limits
Bus | 4 | has not exceeded normal operating limits
Bus | 5 | has not exceeded normal operating limits
Bus | 6 | has exceeded normal operating limits
Bus | 7 | has exceeded normal operating limits
Bus | 8 | has exceeded normal operating limits
Bus | 9 | has exceeded normal operating limits
Bus | 10 | has exceeded normal operating limits
Bus | 11 | has not exceeded normal operating limits
Bus | 12 | has not exceeded normal operating limits